## Sheet1
Market participant | Nr | Document | Question | Answer
Eesti Energia | 1 | FRR dimensioning methodology | he level of detail of the currently proposed methodology which is submitted to the public consultation does not allow market participants to properly validate the methodology as foreseen in Article 11 of SOGL. Please provide a document with sufficient detail (for example, such as Belgium TSO Elia has published: https://www.elia.be/-/media/project/elia/elia-site/public-consultations/2020/20200930_finalreport_en.pdf). For reference, we have attached a report of our own analysis to dimension FCR and FRR needs, and the required volumes for FRR (both aFRR and mFRR) differ considerably from these calculated by TSOs. For example, required aFRR volume in 2025 in our analysis is 1047 MW compared to 134 MW of Baltic TSOs’. In order to understand, what is the reason for such great difference in the results, we need to access and assess the input data. | The input data is described in the FRR dimensioning methodology chapter 3.1. As the input data is collected continously the input data is also changing as new historical data is monitored. Important part of the analysis is the predicted changes in the power system imbalance sources. In the referred report of FCR and FRR dimensioning there have been significant estimates on the solar and wind production growth and it is foreseen that the sources shall continue to produce linearly the same amount of imbalance as it is measured today. Baltic TSOs have not used such high solar and wind production numbers in the analysis and also do not see such scaling of the RES imbalance to be correct way how to approach the RES imbalance effect. As RES production is itroduced to the grid in series of steps, the imabalance these sources create is also introduced to the measurements step by step. If the Baltic imabalances reach such values are brought out in the report the dimensioned values would correspond to the report values, but Baltic TSOs do not see such RES growth feasible for 2025. 1. Baltic TSOs consider that the FRR dimensioning methodology is sufficient in order to conduct FRR calculations. No additional documents will be issued.
Eesti Energia | 2 | FRR dimensioning methodology | How are the HVDC link and >50 MW power plant failures modelled? How long failure durations are modelled (in imbalance)? | HVDC and power plant outages are modelled as probability density function representing the forced outage ratio and potential capacity. Currently Baltic TSOs foresee 2% forced outage ratio for imbalance creation in the probability density functions. Long failure durations are not considered in the calculated model where FRR dimensioning is performed for frequency restoration period, thus long outages are not taken into account.
Eesti Energia | 3 | FRR dimensioning methodology | How is the HVDC link and >50 MW power plant imbalance transferred from aFRR -> mFRR -> RR? With 1 timestep or with a ramp? If with a ramp, at what ramp speed? | The imbalance transfer is a regional phenomen which needs to take into account all the imbalances in individual LFC areas and also LFC block. The aFRR is foreseen to balance the short-term imbalance trends within the 15 minute imbalance window and in case base imbalance is persistent then mFRR should be activated. Both services have set minimum ramp rate - aFRR has full activation time of 5 minutes and mFRR has full activation of 12,5 minutes. aFRR setpoint is continously re-calculated and corrected, while mFRR activation is done for the full 15 minutes period. The transition is not needed to be considered in the FRR dimensioning. RR is not used in Baltic LFC block. The FRR methodology does not consider the imbalace transfer from one product to another. FRR dimensioning is used to assess the FRR needs for the upcomming period using the historical data.
Eesti Energia | 4 | FRR dimensioning methodology | What measurement frequency (averaging period) do the used load and RES forecast error have? | ACE open loop data is calculated as 1 minute average of instantaneous values (up to 10 second data). ACE open loop includes the load and RES forecast errors in normal dimensioning process.
Eesti Energia | 5 | FRR dimensioning methodology | If the forecast errors were not 1-minute averages, how are 1-minute average values calculated for load and RES forecast error? | ACE open loop data is calculated as 1 minute average of instantaneous values (up to 10 second data). ACE open loop includes the load and RES forecast errors in normal dimensioning process.
Eesti Energia | 6 | FRR dimensioning methodology | Which probability distribution functions are used for RES and load forecast error modelling? Why these probability functions were chosen? | The historical RES and load forecast are included in the historical data. No separate probability functions were used for the dimensioning of FRR needs.
Eesti Energia | 7 | FRR dimensioning methodology | How were the probility distribution function parameters scaled for RES capacity forecasts? | Baltic TSOs would collect and use data from similar projects or best practices from areas that have off shore projects implemented. Baltic TSOs agree that adding new type of assets for which no historic data is available can have significant effect, but from the operation moment there will be historical data that will slowly start to influence the ACEol data and will be incorporated in the daily process.
Eesti Energia | 8 | FRR dimensioning methodology | In the future, how would imbalance caused by offshore wind be modelled? For example for the first year, when no historical data is known for Baltic offshore wind parks, but large capacity has just been taken into use. | Baltic TSOs would collect and use data from similar projects or best practices from areas that have off shore projects implemented. Baltic TSOs agree that adding new type of assets for which no historic data is available can have significant effect, but from the operation moment there will be historical data that will slowly start to influence the ACEol data and will be incorporated in the daily process.
Ignitis | 9 | FRR dimensioning methodology | If aFRR dimensioning is performed by estimating the probability of using the 4-hour reserve, then it would be logical to assume that the aFRR capacity won in the auction should be able to be fulfilled by the BSP in the following way during the 4-hour period, by making a mandatory offer to sell/buy balancing electricity | aFRR capacity is dimensioned for 4 hour cycles, but the aFRR is procured for 15 minute validity periods. The dimensioning sets the needed aFRR capacity and does not set requirement for single unit to provide aFRR for the full 4 hour cycle. Limited energy sources are capable to participate both in capacity market and energy market according to market rules.
Ignitis | 10 | FRR dimensioning methodology | Will the Baltic aFRR energy market concept document be adapted accordingly, and in particular point 13 and 33 of the BSP's commitment principles, which sets out the aFRR to be supplied at the auction winning volume? | aFRR capacity is dimensioned for 4 hour cycles, but the aFRR is procured for 15 minute validity periods. The dimensioning sets the needed aFRR capacity and does not set requirement for single unit to provide aFRR for the full 4 hour cycle. Limited energy sources are capable to participate both in capacity market and energy market according to market rules.
Ignitis | 11 | FRR dimensioning methodology | A limitation of the 4 hour period would clearly define the duration of the mandatory bid. This adaptation to the principles of volume determination would be relevant for BSPs with limited energy reservoir (LER) and would lower the entry barrier for participation in the balancing services market. | aFRR capacity is dimensioned for 4 hour cycles, but the aFRR is procured for 15 minute MTUs. The dimensioning sets the needed aFRR capacity and does not set requirement for single unit to provide aFRR for the full 4 hour cycle.
Ignitis | 12 | FRR dimensioning methodology | Please clarify when the reserve quantities will be published. Specifically, point No. 3 in article no.4.2. Suggested wording: "Baltic TSOs and the Baltic LFC block monitor publish the dimensioned FRR, aFRR and mFRR demands for upward and downward direction by D-2 16:00 EET. | The result of FRR dimensioning shall be published 16:00 EET two days in advance of the operation day (the day for which the capacity is procured). It is foreseen that FCR and FRR capacity procurement will take place between 07:30-10:00 EET D-1 (1 day in adavance). To be added in the text.
Ignitis | 13 | FRR dimensioning methodology | The document is numbered for the formulae used. However, there are inaccuracies, please correct accordingly. | Shall be corrected
Taltech | 14 | FRR dimensioning methodology | In enumerated item 3 it is mentioned that “Baltic LFC block is defining the default outage ratio /…/ for /…/ demand units.” It is unclear how large demand units are included in the model? In my opinion this detail should be included in the methodology description. | The effect of demand unit outages is mainly included in the ACEol data as TSOs do not have overview of the grid connection points of large consumers. HVDC export are also considered as demand units and these are included in the list of dimensioning input.
Taltech | 15 | FRR dimensioning methodology | It is claimed that the positive aFRR is "necessary downward regulation" and the negative aFRR is "necessary upward regulation". Meanwhile in [1] it is stated that "7.2.7 Activated aFRR. The sign convention for activated aFRR is: negative value where the LFC area activates downward aFRR, positive value where the LFC area activates upward aFRR." Thus, in my opinion it should be positive aFRR is "necessary upward regulation" and negative aFRR is "necessary downward regulation". | Yes, we shall correct discrepency.
Taltech | 16 | FRR dimensioning methodology | In “Baltic Load-Frequency Control block concept document section 6.5.5.” the mFRR was required to be always larger than aFRR. In Section 3.5 of this document, that requirement is missing. This poses the following risk: if the aFRR need surpasses the (FRR-aFRR), and mFRR needs to replace aFRR reserves by 15th minute, it may not have sufficient capacity to do so, when it is dimensioned for (FRR-aFRR). Thus, maybe when mFRR is dimensioned, it should be made sure that it acquires a value larger than the aFRR. | Baltic TSOs do not see that such situation is realistic that aFRR would significantly exceed mFRR capacity for Baltic FRR dimensioning for overall Baltic LFC block. Therefore Baltic TSOs have not foreseen need for such a requirement in the FRR dimensioning methodology.
Taltech | 17 | FRR dimensioning methodology | It was unclear how, in the future, would imbalance caused by offshore wind be modelled? For example for the first offshore wind farm, when no historical data is known for Baltic offshore wind farms, but large generation capacity will be added to the system. | Baltic TSOs would collect and use data from similar projects or best practices from areas that have off shore projects implemented. Baltic TSOs agree that adding new type of assets for which no historic data is available can have significant effect, but from the operation moment there will be historical data that will slowly start to influence the ACEol data and will be incorporated in the daily process.
Eesti Energia | 18 | Coordinated actions to reduce FRCE | We agree with the currently calculated FRCE level 1 and level 2 limits of 35 MW and 65 MW, respectively. | FRCE target level values are calculated and established by the ENTSO-E subgroup system frequency. These values are checked yearly from the subgroup to verify the LFC block capabilities to keep the system in balance. Please note that the values were not part FRR dimensioning document.
Eesti Energia | 19 | Coordinated actions to reduce FRCE | We would like to stress that all coordinated actions that TSOs make use of to reduce the FRCE must be market-based mechanisms to full extent and be in accordance with EU Regulations 2019/943 and 2017/1485 and Directive 2019/944. The activation of other reserves, which can only be used as a last resort in case all other market-based mechanisms have been exhausted, must also conform to the mentioned EU regulations. | Yes, TSOs foresee using market-based mechanisms to full extent as a priority. All other tools shall conform with EU regulations.
Eesti Energia | 20 | Coordinated actions to reduce FRCE | We would like to point out, that after short-term coordinated actions have been carried out by the Baltic TSOs to reduce FRCE to nominal level, and on a regular basis (e.g. annually), a comprehensive analysis should follow to assess the adequacy of FRCE levels and identify the causes of the violation of FRCE limits. This analysis should always include the questions of : | Such process is established on the Continental Europe synchronous area level. The FRCE values are checked regularly from the subgroup to verify the LFC block capabilities to keep the system in balance. The FRCE levels shall provide overview from the perspective of reserve capacities volumes and operation procedures. In case target levels are breached it will be high-lighted by the analysis and corrective measures need to be provided by given LFC block.
Eesti Energia | 21 | Coordinated actions to reduce FRCE | 1. Whether the Baltic TSOs have dimensioned the necessary amount of frequency restoration reserves properly? | Such process is established on the Continental Europe synchronous area level. The FRCE values are checked regularly from the subgroup to verify the LFC block capabilities to keep the system in balance. The FRCE levels shall provide overview from the perspective of reserve capacities volumes and operation procedures. In case target levels are breached it will be high-lighted by the analysis and corrective measures need to be provided by given LFC block.
Eesti Energia | 22 | Coordinated actions to reduce FRCE | 2. Whether the exceptionally high extent of shared and exchanged reserves in the Baltic LFC block (as proposed by the Baltic TSOs) is adequate to guarantee the operational security of the Baltic LFC block (or whether it should be reduced and, hence, procure more reserves)? | Such process is established on the Continental Europe synchronous area level. The FRCE values are checked regularly from the subgroup to verify the LFC block capabilities to keep the system in balance. The FRCE levels shall provide overview from the perspective of reserve capacities volumes and operation procedures. In case target levels are breached it will be high-lighted by the analysis and corrective measures need to be provided by given LFC block.
Eesti Energia | 23 | Coordinated actions to reduce FRCE | 3. Whether there is enough market-based capacity available to provide the necessary amount of frequency restoration reserves to the market and what can be done to attract more Balancing Service Providers to provide the reserves? | Such process is established on the Continental Europe synchronous area level. The FRCE values are checked regularly from the subgroup to verify the LFC block capabilities to keep the system in balance. The FRCE levels shall provide overview from the perspective of reserve capacities volumes and operation procedures. In case target levels are breached it will be high-lighted by the analysis and corrective measures need to be provided by given LFC block.
Ignitis | 24 | Coordinated actions to reduce FRCE | Is it to be understood that each Baltic TSO will have an FCRE that is predetermined and will control it, but not the LFC block control block error for the whole Baltic area? | Yes, it is foreseen that each LFC area shall control its own FRCE with aFRR and mFRR capacities. By managing the LFC area FRCE-s the Baltic LFC block FRCE is also maintained. In addition the balancing platforms MARI and PICASSO with support of IGCC shall provide a tool for Baltic TSOs for imbalance netting to improve and optimise the FRR activations.
Ignitis | 25 | Coordinated actions to reduce FRCE | If so, why is it necessary to control each of the three LFC areas individually in the context of a common Baltic Balancing Capacity Market, but not to control the LFC block deviation of the whole Baltic LFC block by rotating one responsible operator and implementing a common Baltic LFC controller? Maybe in some extend there is a need to identify Affected TSO and ask for additional measures, but it is not understandable why the help to eliminate FRCE of affected TSO shall be asked by affected TSO instead of LFC block monitoring TSO? | Baltic TSOs have made a decision that each LFC area shall calculate and operate it's own FRCE and balance the system with aFRR and mFRR capacities. Each LFC area shall calculate and provide demand for the balancing platforms, perform imbalance netting and take into account the available transfer capacities between LFC areas. In case LFC block would have single demand then Baltic TSOs would still need to develop internal tools for managing the separate activations. Following the LFC area and balancing platforms model, Baltic TSOs can manage activations with European commonly developed tools.
Ignitis | 26 | Coordinated actions to reduce FRCE | Commission Regulation (EU) 2017/1485 does not require FRCE to be controlled by the each LFC area individually, so we propose to consider the possibility of controlling the control error of all Baltic LFC block collectively, but not individually for each LFC area, to avoid adversarial control within the LFC block, and thus to incur additional costs for the BRPs. | The operation of balancing platforms MARI and PICASSO with support of IGCC shall provide tools to perform imbalance netting and to ensure correct usage of available transfer capacities. Therefore it shall provide more benefit for Baltic TSOs to follow to European commonly developed tools
Ignitis | 27 | Coordinated actions to reduce FRCE | The methodology is generic, and it is not clear to the market participant how operators will coordinate FRCE with operators of other LFC blocks and in what order of priority? | On the Baltic LFC block level the LFC block monitor shall have an overview of the FRCE and identify any violations. The aFRR and mFRR activations are done in accordance with local demand and taking into account the activation requests from balancing platforms. TSO does not set any priorities for the activation. The activation shall be done in accordance to the given validity period merit order list.
Ignitis | 28 | Coordinated actions to reduce FRCE | Can Baltic TSOs explain, how activations will take place in each of the LFC areas in case of breach FRCE limit of are if the Baltics will have a Single Balancing Capacity Market and balancing capacity will be supported for the other LFC area? How LFC controller of LFC area will count this support in case of the activation by BSP in other LFC area? Does the activation will count balancing and disbalance energy correctly in case of bypassing MARI and PICASO during alert state and using measures listed in 1.3? | Baltic TSOs foresee operating with MARI and PICASSO with support of IGCC which shall ensure the availability of appropriate balancing energy market bids. In case connection with MARI or PICASSO shall be unavailable a fallback solution shall be established for the Baltic LFC block.
Ignitis | 29 | Coordinated actions to reduce FRCE | To have a clearer understanding of how Baltic operators will coordinate FRCE minimisation in normal and emergency situations, could you please provide a flow chart of the logical sequence of coordination. | The actual process shall consider the available tools in the operation. The document provides list of actions that can be used and the actual usage shall depend on the availability and the potential effect. Baltic TSOs do not see a need for a flow chart as all actions are plausible.