## Sheet1
Name of consultation: |  | Mechanism for long-term balancing capacity reserve procurement
Consultation started: |  | 2023-12-08
Deadline for feedback: |  | 2023-01-19
Notifications sent to: |  | Market participants in the region
Feedback received: |  | Totally five market participants responded
No | Comment on | Comment | Response from Elering
1 | aFRR requirement | Proposal to remove aFRR requirement when aFRR is not planned to be procured with this procurement. Fulfilling aFRR requirement even in the range of 10% would be a very restrictive factor and exclude some potential assets which would otherwise be eligible to participate in the reserve. | Elering is not aware of such technology which has remarkably higher cost if aFRR-capability in addition to mFRR is added. It is not assumed that the asset, whether successful in mFRR capacity day-ahead bidding or not, will always be ready for aFRR. However, the asset should have the capability to bid for such a product.
2 | Battery restrictions | Full capacity of mFRR up during 24h is very demanding for a battery. | Elering agrees to lower the minimal bid to 25 MW and bid granularity to 1 MW. The 24h requirement is necessary to provide sufficient reserve in case of an outage, which has a longer duration. Such outages are very common and reserves must be available to cover the loss of power until power plants can be started. Such power plants are likely thermal units, which start-up time is several tens of hours.
3 | Battery restrictions | Demanded incontinuous delivery time (24 h) is too demanding for batteries which are optimal in range between 1-4 hours | The purpose of the mechanism is to procure assets that could provide the missing energy during the time generation assets with longer start-up time are able to start.
4 | Battery restrictions | Currently proposed conditions by Elering are too restrictive for BESS to meaningfully participate in the planned capacity reserve markets due to the following reasons: The proposed requirement of 50 MW for 24 hours means 1,200 MWh of storage capacity. However, as the system needs to recharge in 6 hours, a 200 MW grid connection would be needed. Due to continuing limitations in the transmission grid, the number of suitable connection points remains scarce, and access limited | The purpose of the mechanism is to procure an asset that could provide the missing energy during the time generetion assets with longer start-up time are able to start. However Elering agrees to lower the minimal bid to 25 MW and bid granularity to 1 MW
5 | Battery restrictions | The proposed requirement for providing balancing energy for at least 24 hours is not justified in any manner. Suggestion to set the duration to a maximum of 2 hours. It is important to consider that a higher-capacity BESS commands a proportionally higher investment cost. | The purpose of the mechanism is to procure an asset that could provide the missing energy during the time generetion assets with longer start-up time are able to start. However Elering agrees to lower the minimal bid to 25 MW and bid granularity to 1 MW
6 | Battery restrictions | Considering the restrictive nature of the conditions Elering has so far prepared for the planned long-term balancing capacity reserve mechanism towards e.g. BESS, we are concerned that the principles of EU regulation 2019/943 are currently not fully upheld. Therefore, we strongly encourage Elering to review the conditions and impose more flexible market-based solutions, which would allow better access to the balancing market for all market participants. | Elering has prepared the conditions as flexible as possible considering the nature of the needs in Estonian power system. We will consider comments made regarding the BESS.
7 | Bid size/aggregation | We propose to reduce the one unit bid from 50 MW to 25 MW | Elering agrees to lower the minimal bid to 25 MW and bid granularity to 1 MW
8 | Bid size/aggregation | Is the definition of bid unit seen as a single generating asset or the unit size be a combination of multiple assets and/or sites? For example, could four 12.5 MW assets submit a combined single unit bid to fulfil the 50MW criteria? | Combination of multiple assets into single bid will be allowed.
9 | Bid size/aggregation | Unit bid should be a minimum size + granularity (e.g. min 50 MW + 5 MW steps) to adapt for higher capacity assets. | Elering agrees to lower the minimal bid to 25 MW and bid granularity to 1 MW
10 | Bid size/aggregation | We suggest: a certain amount of MW is dedicated to State of Charge Management. The State of Charge management strategy is tested against a statistical of historical data of mFRR activation and the right amount of MW for SoC management is determined to ensure 24h provision of mFRR balancing service. | Elering agrees to lower the minimal bid to 25 MW and bid granularity to 1 MW. However as the lack of possible reserves in Estonia is most likely caused by the outage of Estlink 2 the state of charge management will not be enough to cover the deficit
11 | Bid size/aggregation | Minimal quantity for bidding should be lower (1 MW+) | Elering agrees to lower the minimal bid to 25 MW and bid granularity to 1 MW
12 | Bid size/aggregation | Recommendation for decreasing the minimum unit size to 25 MW, as it is much easier to develop and obtain smaller grid connections. Lowering the bid size will help to increase competition among bidders, thus also leading to more competitive pricing and results. | Elering agrees to lower the minimal bid to 25 MW and bid granularity to 1 MW
13 | Bid size/aggregation | We propose that up to a quarter of the capacity to be procured by the mechanism would be reserved – as a separate slot for bidding - to new build electricity storage solutions and demand response (both single and aggregated solutions). This slot should be treated separately and must not compete with other asset groups, e.g generation. Minimum bid unit for these providers should be no higher than 1 MW. | The purpose of the mechanism is to procure new assets that could provide the missing energy during the time generetion assets with longer start-up time are able to start.
14 | Bid size/aggregation | If single or aggregated consumption assets are able to fulfill reasonable technical conditions they should be able to participate in the procurement. | Combination of multiple assets into single bid will be allowed.
15 | Bid size/aggregation | Decrease bid unit to enable smaller assets and more service provides to participate. This would engage larger pool of potential service providers. We propose that the standard unit of one bid should be 25 MW. For new build storage solutions and demand response the minimum bid unit should be no higher than 1 MW. | Elering agrees to lower the minimal bid to 25 MW and bid granularity to 1 MW
16 | Black start requirement | A Battery Energy Storage System can be designed to provide Black Start, but it required additional CAPEX to oversize the power conversion system in order to inject high amount of reactive current. A possibility should be given to bid with a strike price without Black Start, and an optional Strike Price with Black Start. | Elering agrees to remove the black start requirement.
17 | Black start requirement | “black start requirement” is new to the Estonian market. Therefore, Elering should share technical requirements of black start units, so market participants could prepare their projects accordingly. | Elering agrees to remove the black start requirement.
18 | Black start requirement | Proposal to remove Black Start requirement for consumption assets as this requirement cannot be fulfilled with consumption assets. Meanwhile, upregulation with consumption assets could still provide the necessary reserve. | Elering agrees to remove the black start requirement.
19 | Concern over market distortion | A mechanism will lead to mFRR up capacity bids close to 0€/MW/h with distortion of competition. | Elering does not agree with the conclusion. The mechanism will lead mFRR up capacity bids close to each participant`s asset`s marginal cost.
20 | Concern over market distortion | As it is designed, we see a clear market distortion between assets which have concluded a CfD for mFRR up provision, and those who haven’t. Assets under CfD have a tremendous competitive advantage because they can choose (without any risk) whenever they want to be selected on the mFRR up capacity market, which is not compliant with an open bid market. | Elering does not see market distortion as the auction to be rewarded for CfD creates competition between providers and therefore the CfD price itself should result in economically optimal level. With or without CfD, market participants are incentivised to bid at marginal cost.
21 | Concern over market distortion | Cheap capacities will frequently not provide the service. Expensive capacities will be paid all year long, and be selected whenever cheap capacities leave the market. | Elering does not agree with the conclusion. The mechanism will lead mFRR up capacity bids close to each participant`s asset`s marginal cost.
22 | Concern over market distortion | A bad price signal to trigger new investments or encourage lower prices | Elering does not agree with the conclusion. CfD will incentivise new investments.
23 | Concern over market distortion | Mechanism has an impact on the already decided investments. | Mechanism is designed to intensivize new capacities to enter the market and it is carried by the concern that there are not enough FRR-capable providing units in the market. Therefore, we see procured assets to fill the gap not to take away any market share of existing assets.
24 | Connection terms | We suggest both the financial and technical capability of the bidder, and access to grid be included as additional criteria assessed along the bid price | Grid connection will be the responsibility of the tender participant. However, Elering has made a proposal to change Estonian legislation in a way that would fix the cost of connection in existing grid and standardise more the timeperiod required for connection. Current capapilities for new connections can be found: https://elering.ee/liitumisvoimsuste-rakendus-e-gridmap
25 | Connection terms | Please clarify how you have intented to mitigate the risks regarding grid connection costs and grid availability required to meet the project deadline. | Shall be clarified in the procurement documentation. Current capapilities for new connections can be found: https://elering.ee/liitumisvoimsuste-rakendus-e-gridmap
26 | Connection terms | It would be helpful if certain guarantees about the availability of sufficient biomethane or hydrogen infrastructure and other resources for the operation of these CfD supported plants after 2035 are provided by Elering. | In the frames of CfD Elering can not give any extra warranties. Bidder should base on one`s connection/supply contracts, and current published grid development plans. However Elering is planning to change the structure of gas-grid fees and to implement capacity-based tariff.
27 | Defining "new" asset | Proposal allowing procured assets to be co-located with other generators | Yes, existing connection points can be used for providing the service.
28 | Defining "new" asset | Proposal to open the CfD mechanism for available existing capacities, including the existing thermal fleet. | As the intention of this mechanism is to intensivize investments to new dispatchable capacities, existing capacities will not fall under the mechanism.
29 | Defining "new" asset | Proposal to allow existing assets to participate in the procurement. While it is important to attract new investments, there are also existing generation and consumption assets which could participate in reserve markets if there would be more certainty provided by the mechanism. Existing generation and consumption assets can compete on the basis of extra investments needed to offer reserve capacity (e.g. investments into control systems, efficiency improvements etc) and these assets should not be outright denied to participate in the procurement. | As the intention of this mechanism is to intensivize investments to new dispatchable capacities, existing capacities will not fall under the mechanism.
30 | Fines/deposits/penalties | We suggest that if the asset is not able to meet the deadline due to grid connection issue which can be considered as Elering’s shortcoming, the CfD payments should be made for the period where the asset in not able to participate in the market. | Elering will consider adding the clause to tender conditions.
31 | Fines/deposits/penalties | Please clarify the mechanics of the fine in case of failure to construct on the agreed schedule: Is the fine 100 000€ per MW in total or is it calculated 100 000€ per MW for each year? | In the updated concept document the fine will be defined as 300 € / MW / calender day
32 | Fines/deposits/penalties | Deposit should be returned to unsucessful bidder in accelerated schedule | Elering will consider the proposal.
33 | Fines/deposits/penalties | Fine for not meeting the schedule should depend on the time period. Proposal: 300 €/MW/calender day | In the updated concept document the fine will be defined as 300 € / MW / calender day
34 | Fines/deposits/penalties | Deposit should`nt exceed 500 EUR/MW (instead of 5000 €/MW) | Elering agrees to lower the deposit to 2500 €/MW
35 | Fines/deposits/penalties | Fine for not meeting the schedule should depend on the time period. Proposal: 10000 €/MW/month | In the updated concept document the fine will be defined as 300 € / MW / calender day
36 | Fines/deposits/penalties | It should not be penalised if the project is not completed on time due to external factors beyond promoter’s control, e.g contested EIAs, building permits etc. It should be possible to extend the time of delivery in such cases. | Elering will consider the proposal.
37 | General remark for the design | Given that the day-ahead balancing procurement market does not currently exist, it is difficult to assess the volumes and bid prices of such a market. Without existing market, it is difficult to assess what could be “effective” capacity payment, which creates additional financial uncertainty. The proposed CfD structure does not create a full certainty in which amount the investment could be recovered throughout the contract period. | The size of effective capacity payment should be outcome for this procurement. All participants are expected to assess their possibilities and costs of one`s assets and develop proper strategy for participation. Elering has published a forecast for the needed reserves until year 2031: https://elering.ee/sites/default/files/2022-10/FRR_dimensioning_forecast_2024-2031_0.pdf
38 | General remark for the design | Please consider changing the remuneration mechanism to a fixed fee based on participation instead on two-sided CfD structure – The awarded generator will receive the awarded amount if it participates in the day-ahead procurement, regardless of the results or the market clearing price. Alternatively, if the CfD structure is seen as the preferred remuneration mechanism, we suggest improving the mechanism to provide the certainty of remuneration regardless of whether the Balancing Capacity provider’s bid was successful or not. | Elering will imprope the wording to make it unabigious. It is already foreseen that CfD owner will receive remuneration regardless of whether the Balancing Capacity provider’s bid was successful or not. However CfD owner has obligation to submit bid to the day-ahead capacity market to receive the CfD remuneration.
39 | General remark for the design | Considering that the day-ahead mFRR capacity procurement does not exist yet, please explain how the market is going to operate if, for example the asset will only participate in the mFRR market. Is the following example correct: o During the day-ahead balancing procurement, the TSOs are going to order “readiness service” in certain volume and will pay capacity fee based on the capacity procured (x EUR per MW per each hour procured). o The asset, which was procured day-ahead, will have an obligation to be ready for upward activation in the procured hour. | The example provided is correct. The CfD owner will receive remuneration only if it submits a bid to the day-ahead capacity market. If its bid is successful, it will get the CfD remuneration and is obliged to submit a bid to the FRR energy market as well. If its bid is unsuccessful in the day-ahead capacity market, it will still receive the CfD and can choose to participate in the day-ahead or intraday electricity market and FRR energy market. If it does not submit a bid to the day-ahead capacity market, it will not receive CfD remuneration; however, it can still participate in all other markets. In order to receive the Strike Price of one`s CfD the bid to mFRR energy market will be mandatory
40 | General remark for the design | In each hour, energy bid prices of all mFRR bidders will be in the same merit order, regardless of on whether an asset was procured day-ahead or not. It means that if energy bid price is too high, the asset may not be activated. ▪ For example, 200 MW was procured day-ahead, asset B was awarded. During a certain hour, TSO activates in total 300 MW of mFRR capacity. Since in that hour there was additional hourly mFFR capacity offered, and asset B bid was not among 300 MW with the lower price, asset B will not be activated. | Any asset successful in the day-ahead capacity market is obliged to submit a bid to the FRR energy market and must be ready for activation. The merit order of FRR energy market bids is not dependent on whether the asset participated in the day-ahead capacity market or not.
41 | General remark for the design | Are there any rules for the bids to the day-ahead energy market for successful mFRR capacity bidders (e.g. minimum or maximum price or marginal cost-based pricing?) | Elering expects the bidding to both capacity and energy markets to be marginal cost based.
42 | General remark for the design | If the capacity will not be procured, it still can offer volumes in intra-day mFRR market, or other markets (such as day-ahead wholesale market) | If the capacity bid was unsuccessful then participating on other markets is allowed. However, in order to receive compensation from Elering, reserve energy market bids must be made.
43 | General remark for the design | A mechanism will not guarantee that contracted capacities will offer mFRR up services at critical moments | Elering assumes this to be rare occurence. Elering assumes that due to critical moment the balancing products will have relatively high price on the market and all the assets are intensivized to bid on the reserves energy market due to that.
44 | General remark for the design | There is a risk for ELERING, during low energy prices, to always pay the full amount of Strike Price to all CfD awarded players | Elering does not agree with the conclusion. The mechanism will lead mFRR up capacity bids close to each participant`s asset`s marginal cost.
45 | General remark for the design | Proposal for the mechanism change: Assets under CfD on mFRR up capacity remuneration shall not bid on the market. Those assets shall be considered as Reserve Assets which shall be selected by ELERING whenever ELERING cannot procure sufficient mFRR up capacity from the market : • If the market offers enough capacity : ELERING could select the cheapest offers from the market, up to the Strike Price of the Reserve Assets, and complement with Reserve Assets. • If the market doesn’t offer enough capacity, or too expensive capacities compared to Reserve Assets, ELERING could select Reserve Assets only, and complete with market based assets if not sufficient. | Elering will consider the proposal, however, the proposal apperas to increase the costs of reserve provision to the Estonian consumer.
46 | General remark for the design | As an obligation with this CfD contract, Reserve Assets should have an obligation to be available for selection, for example, over a certain number of days per year. For example, 150 days per year, Reserve Assets are forced to offer their capacity without compete in the mFRR up capacity market. Each day ( of this 150 days), after the auction, Elering will inform each the BSP with Cfd if its Reserve Capacity is finally needed or not. If the Reserved Capacity is finally needed, they provide the mFRR up service in the same conditions as other market players, but their capacity remuneration is set at the Strike Price level. If not selected, they can act on other markets and their capacity remuneration is set at the Strike Price level minus the mFRR up market price. | Elering will consider the proposal, however, the proposal apperas to increase the costs of reserve provision to the Estonian consumer.
47 | General remark for the design | Will the Strike Price be unique for all selected bidders? Or will there be different strike prices for each bidder? How will the procurement exactly happen? | Each bidder gets the strike price one has offered in the procurement. Each bidder will have different strike price.
48 | General remark for the design | Will Elering publish the Strike Price for each selected winner? | According to Public Procurement Act all submitted quotations will be published.
49 | General remark for the design | What happens if Capacity Providers bids all the time at 0 Eur/MW/h? What will be the process to chose the best offer? | On the mFRR capacity market, cheapest bids are chosen which meet the mFRR demand. 0 price for all demand is unlikely. Should this happen, curtailment of bids will be undertaken, subject to bid divisibility information.
50 | General remark for the design | Contract period should concider lifetime of a batteries. I.E. lithium batteries can last up to 10000 cycles and contain up to 70% of the initail capacity after that. | Lifetime of assets is for the bidder to assess. Elering follows the need for balancing products and it`s technical capapility. The lenght of contract will be determined with EC deisicion.
51 | General remark for the design | Can the bidder use the same (existing) connection point with production unit? | Yes, existing connection points can be used for providing the service.
52 | General remark for the design | Will the contracted unit be allowed to participate in other markets? | Yes.
53 | General remark for the design | If the capacity market is meant only for up-regulation bids and the battery offers its capacity for the next day, then can it at the same time offer downregulation in the energy market? | Yes, if state of charge enables fulfilling requirements of up-regulation market.
54 | General remark for the design | If the offer is made for 24 hours, there is a 6 hours charging period, and the battery is activated during 16:00-24:00, then can it still get CfD payment for capacity for the next 24 hours even though it is not able to provide the full capacity, but only maximum 16 hours? | CfD remuneration is foreseen only for those market time units (MTU = 15 min) when bid was placed to the day-ahead capacity market. If the bid was succesfull at the capacity market one must place bid also to reserve energy market for those MTUs and must be ready for activation if needed. Therefore CfD owner can submit bid only for those hours when it can be activated.
55 | General remark for the design | Proposal that both mFRR upregulation and down-regulation will be procured together. | As Elering does not foresee the lack of downward regulation mFRR providers the CfD-contract is only for upward regulation.
56 | General remark for the design | The terms and conditions of the future contract should allow for the unit to commence operations earlier than the date after which the calculation of penalties will begin. I.e., a buffer time should be permitted so that if the project is completed earlier, it would already be able to participate in the market. | It is in Elering`s interest to have the asset connected to the grid as soon as possible. CfD starts when asset is commissioned.
57 | General remark for the design | Elering should make it clear how they will compare the offers from two or more units submitted to the tenderer based on their proposed CfD limits. This will give the developers clarity whether their projects are competitive. Proposal to rank projects based on their bottom CfD, i.e., the minimum subsidy that they request | Indeed, Elering plans to compare bids based on offered price, preferring lower prices.
58 | General remark for the design | If Elering has conducted any studies about (long-term) balancing capacity reserve schemes in other countries, this data should be shared with market participants, so that they would have more background knowledge when preparing to submit bids. | According to our understanding, long-term balancing capacity agreements require derogation from EU legislation and, therefore, similar schemes do not exist.
59 | General remark for the design | We caution against use of TSO assets (according to articles 40(4) and 54(2)) as this would indeed have detrimental effect on any market-based initiative. Therefore we urge Elering to state it upfront, clearly and unambiguously that it will not make use of these derogations. | Elering states that the TSO assets will be used for the period only up to three years from the syncronization to CE-grid according to electricity market reform derogation.
60 | General remark for the design | Compared to implementation of a market-wide capacity mechanism for new builds in Europe and the planned mechanisms in Sweden and Finland , the current proposed mechanism for procurement of long-term balancing reserves may not be sufficient to provide certainty for actual investment decisions. Therefore an enhanced capacity mechanism is required. | Elering shall evaluate further need for capacity mechanism as a different process and timeline.
61 | General remark for the design | For certain type of combined cycle gas turbines it is necessary to keep them running in certain load (40-50% of net capacity) in order to be able to provide mFRR. If in case of such unit with net capacity of 200 MW should come to market then can it participate in the procurement with 200 MW mFRR? | Such unit can participate with the amount of mFRR which it is prequalified for. By the given description the amount of possible mFRR seems to be around 100 MW (50-60% of net capacity)
62 | Maintanence period | Please clarify the inclusion of maximum maintenance period per year is 45 calendar days when there is no obligation to participate in the day-ahead auctions. | The mechanism's idea is to increase the overall installed reserve capacity in the electricity system. Therefore, even though there is no obligation for the successful CfD-contract winner to make the bid to day-ahead capacity market it is mandatory to be available in the grid. As all generating/storage need to be maintained after every certain period it is necessary to specify the period. Elering reserves the right to assess the availability of resources under CfD contract.
63 | Maintanence period | Maintenance period 45 days/year could be smaller | Proposed maintainence period is chosen with intention to treat all possible technologies neutrally.
64 | Maintanence period | Reasonable periods per year should be provided for capacity resources during which they do not need to submit any bids to the reserve market (planned and unplanned outages, emergencies, etc). | In the concept document 45 days per year maintanence period has been foreseen for the assets
65 | Maintanence period | Assumably the amount of capacity is concidered as net capacity. If in case of unplanned outage a part or whole of contracted capacity is unavailabe, will the provider be fined if the offered capacity bid is not followed by energy bid? | Elering considers adding unplanned outages to 45 day service period.
66 | Timeline | Please clarify the expected timeline of finalized structure announcement and details of the mechanism deadline. | In order to introduce the measure, a derogation is needed from EU legislation to enable long-term procurement of reserves. The timeline of the derogation is uncertain, however, Elering expects such derogation mid 2024. Final details of the measure will be provided in the procurement documents.
67 | Timeline | Please clarify the timeline from finalized structure announcement to the announcement of the tender and the awarded projects. deadline. | Shall be clarified in the procurement documentation. Presently Elering expects a procurement duration of 6 months.
68 | Timeline | Is the approved state aid decision a prerequisite of announcing a tender? We suggest that once the tender conditions are finalised, the tender should be announced immediately to speed up the process, assuming the positive state aid decision will be granted during the tender. | Please note that there is no state aid decision needed for capacity procurement mechanism if a derogation is provided to Estonia in from Article 6(9), (10) and (11) of Regulation 2019/943. As the specifics of the derogation might have great effect on the overall terms, Elering finds it is not feasible to announce the tender prior to final derogation deicision from the EC
69 | Timeline | Theoretical start of the contract (assuming the project can meet the deadline) – is it from joining the continental European synchronous area or is other start time foreseen? | The soonest theoretical start is the date of joining European syncronous area.
70 | Timeline | The ongoing process and timeline of the state aid decision from the EC – will the draft state aid notification be introduced to interested parties to allow comments; when are your expecting to have the confirmation whether such measure will be approved by the EC; | Please note that there is no state aid decision needed for capacity procurement mechanism if a derogation is provided to Estonia in from Article 6(9), (10) and (11) of Regulation 2019/943. As per Elering's knowledge, the decision on the derogation is in the final stage, and an official notification is expected in March 2024.
71 | Timeline | The ongoing process and timeline of the trilogues for the derogation from Article 6(9), (10) and (11) of Regulation 2018/943 – when are you expecting to have the confirmation of whether such derogation shall be approved. | As per Elering's knowledge, the decision on the derogation is in the final stage, and an official notification is expected in March 2024.
72 | Timeline | Could you please clarify why the derogation from the Article 6(9), (10) and (11) of Regulation 2018/943 is sought only for 8 years after synchronization and what prevents seeking derogation for longer period. | Longer period was seeked, 8 years is the compromise received.
73 | Timeline | How is the construction schedule agreed and whether there is a possibility to amend the construction schedule during the construction period? | The general idea is to apply the rules of the derogation, which forsees start of providing the service latest 5 years from signing the contract. The earlier the start of providing the service, the longer the period of CfD application.
74 | Timeline | Shorter delivery time (2-3 years from signing the contract) would be propriate. | Shorter delivery times are allowed. The faster the start of service, the longer the period with CfD contract.
75 | Timeline | Tender timeline should be shorter (4 months instead of 6 months) | Elering will consider the proposal.
76 | Timeline | For a new-build flexible generation project, if project development would commence today and it would be necessary to carry out all development tasks and requirements in full a reasonable estimate for the start of operation of a new-build facility is no earlier than in the year 2030. 3 years is a very short period for a CfD contract | The period is limited with the derogation from EC to 8 years staring from the syncronisation to central-Europe syncronization area
77 | Timeline | We propose that given the shortness of the effective CfD support period, Elering should pursue every avenue to make sure that after 2033 it would continue to use CfD procurement instrument with maximum durations (e.g at least 1 year), for a period of at least 10 years to lower the overall cost of reserves. | The period is limited with the derogation from EC to 8 years staring from the syncronisation to cerntal-Europe syncronization area. Please not that the day-ahead capacity market and possibility to participate in the market shall continue also after the CfD contract will end
78 | Timeline | The CfD period should preferrably be longer (12-15 yrs); | The period is limited with the derogation from EC to 8 years staring from the syncronisation to cerntal-Europe syncronization area
79 | General remark for the design | If in case of successful service provider has signed CfD contract for certain amount of MW (as example 200 MW) and for certain MTU the need for mFRR up is less (as example 150 MW) then in which amount of capacity will the service provider be guaranteed the price of? | Each service provider which has been successful in CfD contract procurement will be guaranteed the price in full amount of contract (by the provided example 200 MW).
80 | General remark for the design | It is stated in the document the maximum allowed emitted CO2 level is 550 kg/MW. Will the demanded level be the same after CfD contract period (after y 2033) or will that change? | The CO2 demand is not CfD-procurement specific and is initiated from European regulation. Current Estonian demand is specified in "Atmosfääriõhu kaitse seadus" (https://www.riigiteataja.ee/akt/122092023001?leiaKehtiv)
81 | General remark for the design | Is battery concidered as "all end customer" and should one pay all the grid fees accordingly? | Batteries are concidered as all end consumers at the time of charging and therefor all the grid fees (including renewable energy fee) and taxes apply.
82 | General remark for the design | Please specify numerically which is minimal necessary net power and energy capacity of battery or other energy storage device. I.E if a 25 MW battery must provide the service 24 concequentive hours | In case of no additional clarifications are presented by service provider 24 x 25 = 600 MWh capacity battery would meet the demand.If provider should have a device connected directly to storage unit which allows to charge in the middle of delivery period the capacity demand could be reduced accordingly.
83 | General remark for the design | Please specify the minimal state of charge rate for the battery to provide the service. | As it is not mandatory to make the bid for 24 h delivery unit the state of charge held in the battery should be at the level to be able to provide the service as offered in the capacity market. I.E. if the bid is made for 1 h in amount of 5 MW and the asset is pure battery the state of charge kept in battery is 1 x 5 = 5 MWh.
84 | General remark for the design | As 24h delivery is only mandatory to be proven in prequalification it will be interesting for the battery owner to keep the device in 50% SOC level in order to make bids both upward and downward direction. That leads to only up to 12h maximum possible delivery period. | Yes, that is correct. The purpose of the measure is not to make it mandatory for the successful CfD-contract holder to only bit in 24h concequitive bids but the asset operator is free to participate any market.
85 | General remark for the design | Please specify what exactly is meant by "device". Would a electricity network with batteries and windmills connected to it qualify as "device" | The set condition requires the device to be dispatchable. Therefor electricity network would not qualify.
86 | General remark for the design | Proposal to put in place a few safeguards to select the more competitive assets and to adjust the overall revenue generated by the asset under the CfD scheme. ● Selection of the bidder based on lowest overall cost for the public support scheme CfD bidders should provide, at bidding stage, their provisional business plan with the assumptions of CAPEX, OPEX, market revenues (energy and balancing services) including the calculation formula of the Strike Price. The provisional business plan should include the number of hours that the asset is foreseen to be active on the mFRR capacity market (with the number of hours being selected and number of hours being not selected). This will settle the overall amount of CfD additional revenues that is foreseen to be received by the asset in order to balance the business plan. This will also enable the identification of the expected share of CAPEX that will be amortized through participation to the mFRR up capacity market. The bidder should communicate at bidding stage: • the target internal return rate that the CfD should guarantee. • the Strike Price • the overall additional revenues expected from the CfD mechanism The selection criteria for the CfD tender shall not be based on lowest Strike Price, but on lowest overall cost for the CfD support scheme. ● Financial audits of CfD contracted assets CfD contracted assets should provide to the National Regulatory Authority for financial audit purpose: o At commissioning, real CAPEX expenditures and variation according to assumptions at bid stage o At the end of each fiscal year, real OPEX expenditures and markets revenues (on all markets, including mFRR up capacity revenues under CfD contracts). ● Strike Price or CfD duration adjustment according to actual earnings Based on financial data provided by the asset owner, adjustment of the CfD contract shall be made with either Strike Price adjustment, or CfD duration adjustment. Strike Price (or CfD duration) shall be reduced in case of excess of revenues. Strike Price (or CfD duration) shall be increased in case of lack of revenues (up to a regulatory limit). The calculation of Strike Price variation shall be done by adjusting the business plan with updated costs and forecasts, and with a calculation that will enable the investor to maintain the target internal return rate that was communicated at the CfD bidding stage. Limitation on overall additional revenues from the CfD support scheme At bidding stage, a candidate may claim a very low amount of additional revenues from the CfD, and thus ask for a low strike price, or a high strike price but with limited number of hours being active on the mFRR up capacity market. During operation, the asset would then request more to keep the business plan sustainable. Other candidates, at bidding stage, could have been rejected due to higher strike price/overall costs. Consequently, to maintain fair competition, and avoid subsequent disputes arising from CfD tender candidates, a limitation to the increase of Strike Price or Contract Duration shall be settle from the start. | Elering acknoledges the risk and conciders different measures to avoid market distortion but TSO is not in position to obligate the NRA for such surveillance.
87 | Timeline | Proposal to postpone the announcement of procurement for one year so the deadline for submitting the offers would be in summer-autumn 2025 | Elering conciders the proposal but emphasizes that extending the offer submitting period decraeses the contract period for the service provider.
88 | Timeline | What is the rough estimation for the procurement announcement time? | By current estimation the announcement will be made in summer 2024