## Sheet1
SIGNAALID ELEKTRISÜSTEEMI JUHTIMISKESKUSESSE
SÜNKROONGENERAATORITEGA TOOTMISSEADE
Positsioon | Andmetüüp | IEC Aadress | Nimi | Olek | Kirjeldus | Väärtus
1 | C_DC_NA | 1 | Primaarreguleerimine | Töösse/Välja | Primary regulation | 10=On,01=Off
2 | C_DC_NA | 2 | Sekundaarreguleerimine | Töösse/Välja | Secondary regulation (will allow control center to operate P control) | 10=On,01=Off
3 | C_SC_NA | 3 | TS juhtimine U=const | Töösse | Reactive power control algorithm U=const** | On=1,Off=0
4 | C_SC_NA | 4 | EJ juhtimine Q=const | Töösse | Reactive power control algorithm Q=const** | On=1,Off=0
5 | M_ME_NA | 1001 | TS CXT XXX kV Uab | kV | For each 110 kV transformer separately | kV
6 | M_ME_NA | 1002 | TS CXT XXX kV P | MW | For each 110 kV transformer separately | MW
7 | M_ME_NA | 1003 | TS CXT XXX kV Q | Mvar | For each 110 kV transformer separately | Mvar
8 | M_ME_NA | 1004 | TS CXT XXX kV Ia | A | For each 110 kV transformer separately | A
9 | M_ME_NA | 1005 | TS GX XX kV P | MW | For each generator separately, medium voltage side | MW
10 | M_ME_NA | 1006 | TS GX XX kV Q | Mvar | For each generator separately, medium voltage side | Mvar
11 | M_ME_NA | 1007 | TS XXX kV P maksimum | MW | Maximum net generation, given in connection point (XXXkV) | MW
12 | M_ME_NA | 1008 | TS XXX kV P miinimum | MW | Minimum net generation, given in connection point (XXXkV) | MW
13 | M_ME_NA | 1008 | TS XXX kV P sätted | MW | Setting value of P control (feedback) | Pmin…0...Pmax, step 1MW
14 | M_ME_NA | 1009 | TS XXX kV Q sätted | Mvar | Setting value of Q control at Q=const (feedback) | Qmin…0…Qmax, step 1 Mvar
15 | M_ME_NA | 1010 | TS XXX kV Uab sätted | kV | Setting value of Q control at U=const (feedback) | 110...123kV, step 1 kV
16 | M_ME_NA | 1011 | TS statism | % | Setting value of droop (feedback) | 2…8 %, step 1 %
17 | M_ME_NA | 1012 | TS kiirusregul. tundetus | mHz | Setting value of dead band for turbine speed regulator (feedback) | .-500 mHz…0…500 mHz,
step 10 mHz
18 | M_ME_NA | 1013 | TS Pth | MW | Thermal load* | MW
19 | M_ME_NA | 1014 | 110/xx jõutrafo astmelüliti aste | nr | Position of 110 kV step-up transformer's tap-changer
20 | M_ME_NA | 1015 | GX XXX kV F | Hz | Generator frequency (measured at generator's terminals)
21 | M_ME_NA | 1016 | GX XXX kV Uab | kV | Generator Voltage
22 | M_DP_TA (TB) | 2001 | TS XXX kV VL xxx | Sees/Väljas | Curcuit breaker, for each bay separately | 10=On,01=Off
23 | M_DP_TA (TB) | 2002 | TS XXX kV LL xxx | Sees/Väljas | Disconnector, for each bay separately | 10=On,01=Off
24 | M_DP_TA (TB) | 2003 | TS XXX kV ML xxx | Sees/Väljas | Earthing switch, for each bay separately | 10=On,01=Off
25 | M_DP_TA (TB) | 2004 | TS CXT ML xNx | Sees/Väljas | Earthing switch of transformer neutral, for each earthing swich separately | 10=On,01=Off
26 | M_DP_TA (TB) | 2005 | TS GX XX kV VL xxx | Sees/Väljas | Curcuit breaker, medium voltage. For each generator separately | 10=On,01=Off
27 | M_SP_TA (TB) | 3001 | Primaarreguleerimine | Töös/Väljas | Primary regulation (feedback) | On=1,Off=0
28 | M_SP_TA (TB) | 3002 | Autom.primaarreg.töö | Tekkis/Tagastus | Automatic primary regulation operated, 5% (feedback) | On=1,Off=0
29 | M_SP_TA (TB) | 3003 | Avar.primaarreg.töö | Tekkis/Tagastus | Emergency primary regulation operated, 12,5% (feedback)
30 | M_SP_TA (TB) | 3004 | Sekundaarreguleerimine | Töös/Väljas | Secondary regulation (feedback) | On=1,Off=0
31 | M_SP_TA (TB) | 3005 | TS juhtimine U=const | Töös/Väljas | Reactive power control algorithm U=const (feedback) | On=1,Off=0
32 | M_SP_TA (TB) | 3006 | TS juhtimine Q=const | Töös/Väljas | Reactive power control algorithm Q=const (feedback) | On=1,Off=0
33 | M_SP_TA (TB) | 3007 | TS CXT(LYYY) kaitse rike | Tekkis/Tagastus | Power plant CXT transformer protection failure for each transformer separately. | On=1,Off=0
If 110 kV line LYYY protection exist, then its "failure" signal must be sent to the Main Grid (MG) RCC-s as independently
34 | M_SP_TA (TB) | 3008 | TS CXT(LYYY) kaitse | Töötas/Tagastus | Power plant (CHP) CXT transformer protection "operated" signal for each transformer separately. | On=1,Off=0
If 110 kV line LYYY protection exist, then its "operated" signal must be sent to the Main Grid (MG) RCC-s as independently
35 | M_SP_TA (TB) | 3007 | Omatarbele eraldumine | Tekkis/Tagastus | Signal for identifying tripping to houseload operation
36 | C_SE_NA | 6201 | TS XXX kV P sätted | MW | Setpoint value of P control. The value of active power contol speed must be | Pmin...Pmax, step 1MW
according to by Estonian Grid prescription remarked value of power plant totally installed nominal active power value (MW/min).
37 | C_SE_NA | 6202 | TSXXX kV Q sätted | Mvar | Setting value of Q control at U=const | Qmin…0…Qmax, step 1 Mvar
38 | C_SE_NA | 6203 | TS XXX kV Uab sätted | kV | Setting value of U control at Q=const | 110...123kV, step 1 kV
39 | C_SE_NA | 6204 | TS statism | % | Setting value of droop | 2…8 %, step 1 %
40 | C_SE_NA | 6205 | TS kiirusregul. tundetus | mHz | Setting value of dead band for turbine speed regulator | 0…500 mHz, step 10 mHz
Tuule- ja/või päikeseelektrijaam (Läbi inverteri ühendatud tootmisseade)
Positsioon | Andmetüüp | IEC Aadress | Nimi | Olek | Kirjeldus | Väärtus
1 | C_DC_NA | 1 | P avariipiirang 80% | Välja/Töösse | Emergency limit 80% of active power | 10=On,01=Off
2 | C_DC_NA | 2 | P avariipiirang 60% | Välja/Töösse | Emergency limit 60% of active power | 10=On,01=Off
3 | C_DC_NA | 3 | P avariipiirang 40% | Välja/Töösse | Emergency limit 40% of active power | 10=On,01=Off
4 | C_DC_NA | 4 | P avariipiirang 20% | Välja/Töösse | Emergency limit 20% of active power | 10=On,01=Off
5 | C_DC_NA | 5 | Tuulepargi töö | Välja/Sisse | Windpark operation on/off | 10=On,01=Off
6 | C_DC_NA | 6 | Primaarreguleerimine | Välja/Töösse | Primary regulation | 10=On,01=Off
7 | C_DC_NA | 7 | Sekundaarreguleerimine | Välja/Töösse | Secondary regulation (will allow control center to operate P control) | 10=On,01=Off
8 | C_SE_NA | 6201 | XXX kV P sätted | MW | Setting value of P control | Pmin…Pmax, step 1MW
9 | C_SE_NA | 6202 | XXX kV Q sätted | Mvar | Setting value of Q control at Q=const | Qmin…Qmax, step 1MVar
10 | C_SE_NA | 6203 | XXX kV Uab sätted | kV | Setting value of Q control at U=const | 110...121kV (330…362kV),
1kV step
11 | C_SE_NA | 6204 | statism | % | Setting value of droop | 2…8 % (step 1 %)
12 | C_SE_NA | 6205 | sagedusregul. tundetus | mHz | Setting value of dead band for frequency-sensing power controller | .-500 mHz…0…500 mHz
(step 10 mHz)
13 | C_SE_NA | 6206 | P languse kiirus | MW/min | Active power ramp rate, decrease (MW/min) | MW/min (step 1MW/min)
14 | C_SE_NA | 6207 | P tõusu kiirus | MW/min | Active power ramp rate, raising (MW/min) | MW/min (step 1MW/min)
15 | C_SC_NA | 801 | juhtimine U=const | Töösse | Reactive power control algorithm U=const or see below | On=1
16 | C_SC_NA | 802 | juhtimine Q=const | Töösse | Reactive power control algorithm Q=const or see above | On=1
17 | M_ME_NA | 1001 | Tuule kiirus | m/sek | Wind speed | m/sek
18 | M_ME_NA | 1002 | Tuule suund | deg | Wind direction | deg
19 | M_ME_NA | 1003 | Õhu temperatuur | C | Air temperature | C
20 | M_ME_NA | 1004 | Õhu rõhk | mbar (hPa) | OPTIONAL | mbar (hPa)
22 | M_ME_NA | 1006 | Päikeseintensiivsus | W/m2 | Irradiation | W/m2
23 | M_ME_NA | 1007 | võimalik P | MW | Theoratically possible P (10'average+WTG status) | MW
24 | M_ME_NA | 1008 | võimalik Q+ | MVar | Theoratically possible Q+ (10'average+WTG status) | MVar
25 | M_ME_NA | 1009 | võimalik Q- | MVar | Theoratically possible Q- (10'average+WTG status) | MVar
26 | M_ME_NA | 1010 | Tööst väljas olev P | MW | Sum of WTG Pn broken/in mainenance | MW
27 | M_ME_NA | 1011 | Ületuulest kasutamatu P | MW | Sum of WTG Pn not usable from over-wind | MW
28 | M_ME_NA | 1012 | Alatuulest kasutamatu P | MW | Sum of WTG Pn not usable from under-wind | MW
29 | M_ME_NA | 1013 | XXX kV P sätted | MW | Setting value of P control (feedback) | Pmin…Pmax, step 1MW
30 | M_ME_NA | 1014 | XXX kV Q sätted | Mvar | Setting value of Q control at Q=const (feedback) | Qmin…Qmax, step 1MVar
31 | M_ME_NA | 1015 | XXX kV Uab sätted | kV | Setting value of Q control at U=const (feedback) | 110...121kV (330…362kV),
1kV step
32 | M_ME_NA | 1016 | P languse kiirus | MW/min | Active power ramp rate, decrease (1MW/min), (feedback) | MW/min
(step 1MW/min)
33 | M_ME_NA | 1017 | P tõusu kiirus | MW/min | Active power ramp rate, raising (1MW/min), (feedback) | MW/min (step 1MW/min)
34 | M_ME_NA | 1018 | statism | % | Setting value of droop (feedback) | 2…8 % (step 1 %)
35 | M_ME_NA | 1019 | sagerusregul. tundetus | mHz | Setting value of dead band for frequency-sensing power controller (feedback) | .-500 mHz…0…500 mHz
(step 10 mHz)
36 | M_ME_NA | 1020 | XXX kV Uab | kV | SUBSTATION MEASURING, high voltage | kV
37 | M_ME_NA | 1021 | XXX kV P | MW | SUBSTATION MEASURING, high voltage | MW
38 | M_ME_NA | 1022 | XXX kV Q | MVar | SUBSTATION MEASURING, high voltage | MVar
39 | M_ME_NA | 1023 | XXX kV Ia | A | SUBSTATION MEASURING, high voltage | A
40 | M_DP_TA (TB) | 2001 | Tootmisseadme töö | Väljas/Sees | Plant operation on/off (feedback) | 10=On,01=Off
41 | M_DP_TA (TB) | 2002 | GXX staatus | Väljas/Sees | Plant turbine GXX status on/off (feedback for each single turbine in a park)
42 | M_DP_TA (TB) | 2003 | XXX kV VL xxx | Väljas/Sees | SUBSTATION EQUIPMENT CONTROL, curcuit breaker, high voltage | 10=On,01=Off
43 | M_DP_TA (TB) | 2004 | XXX kV LL xxx | Väljas/Sees | SUBSTATION EQUIPMENT CONTROL, disconnector, high voltage | 10=On,01=Off
44 | M_DP_TA (TB) | 2005 | XXX kV ML xxx | Väljas/Sees | SUBSTATION EQUIPMENT CONTROL, earthing switch, high voltage | 10=On,01=Off
45 | M_DP_TA (TB) | 2006 | XXX kV ML xNx | Väljas/Sees | SUBSTATION EQUIPMENT CONTROL, neutral point earthing switch, high voltage | 10=On,01=Off
46 | M_DP_TA (TB) | 2007 | XXX kV liini VL xxx | Väljas/Sees | SUBSTATION EQUIPMENT CONTROL, curcuit breaker, medium voltage line | 10=On,01=Off
47 | M_SP_TA (TB) | 3001 | Prim.reguleerimine | Töös/Väljas | Primary regulation (feedback) | On=1,Off=0
48 | M_SP_TA (TB) | 3002 | Autom.primaarreg.töö | Tekkis/Tagastus | Automatic primary regulation operated, 5% (feedback) | On=1,Off=0
49 | M_SP_TA (TB) | 3003 | Avar.primaarreg.töö | Tekkis/Tagastus | Emergency primary regulation operated, 12,5% (feedback)
50 | M_SP_TA (TB) | 3004 | Sekundaarreguleerimine | Töös/Väljas | Secondary regulation (feedback) | On=1,Off=0
51 | M_SP_TA (TB) | 3005 | juhtimine U=const | Töös/Väljas | Reactive power control algorithm U=const (feedback) | On=1,Off=0
52 | M_SP_TA (TB) | 3006 | juhtimine Q=const | Töös/Väljas | Reactive power control algorithm Q=const (feedback) | On=1,Off=0
53 | M_SP_TA (TB) | 3007 | P avariipiirang 80% | Töös/Väljas | Emergency limit 80% of active power (feedback) | On=1,Off=0
54 | M_SP_TA (TB) | 3008 | P avariipiirang 60% | Töös/Väljas | Emergency limit 60% of active power (feedback) | On=1,Off=0
55 | M_SP_TA (TB) | 3009 | P avariipiirang 40% | Töös/Väljas | Emergency limit 40% of active power (feedback) | On=1,Off=0
56 | M_SP_TA (TB) | 3010 | P avariipiirang 20% | Töös/Väljas | Emergency limit 20% of active power (feedback) | On=1,Off=0
57 | M_SP_TA (TB) | 3012 | (L)YYY kaitse | Töötas/Tagastus | Park transformer YYY protection or line LYYY protection operated, high voltage. | On=1,Off=0
If both, high voltage windpark transformer protection and windpark line protection exist, then their "operated" signals must be sent to the MG RCC-s as two different independent protection operated signals
XX kV, XXX kV pingeklass, voltage class (for example 10 kV or 110 kV)
LYYY liini tähis, line marking
CXT jõutrafo tähis, transformer marking, X is marking number of transformer
GX generaatori tähis, generator marking; X is marking number of generator
xxx operatiivtähistus, operating mark
* - for CHP plants only
** - if Q=const is is locally/remotely activated, U=const is automatically deactivated and if Q=const is locally/remotely deactivated, U=const is activated automatically