## Sheet1
Signal volume required for type C power-generating modules
ENERGY PARK MODULE
Position |  | Data type |  | IEC address |  | Name | Status |  |  | Description | Value
CONTROL SIGNALS AND FEEDBACK
SIGNALS REQUIRED FOR FREQUENCY STABILITY
1 |  | C_DC_NA |  | 1 |  | Primary control (FCR) | On/Off |  |  | Primary control (FCR) 10% | 10 = On, 01 = Off
2 |  | C_SE_NA |  | 6201 |  | droop | % |  |  | Droop setpoint | 2-12%, with step 1%
3 |  | C_SE_NA |  | 6202 |  | frequency controller dead band | mHz |  |  | Frequency controller dead band setpoint | 0-500 mHz, with step 10 mHz
4 |  | M_DP_TA (TB) |  | 3001 |  | Primary control (FCR) | On/Off |  |  | Primary control (FCR) 10% (feedback) | On = 1, Off = 0
5 |  | M_ME_NA |  | 1001 |  | droop | % |  |  | Droop setpoint (feedback) | 2-12%, with step 1%
6 |  | M_ME_NA |  | 1002 |  | frequency controller dead band | mHz |  |  | Frequency controller dead band setpoint (feedback) | 0-500 mHz, with step 10 mHz
SIGNALS REQUIRED TO ENSURE FREQUENCY STABILITY OR REGIONAL STABILITY
ACTIVE POWER CONTROL BY SETTING WITH RAISE AND DECREASE RATE
7 |  | C_DC_NA |  | 2 |  | Active power control (AGC, aFRR, mFRR) | On/Off |  |  | Active power control (AGC, aFRR, mFRR) | 10 = On, 01 = Off
8 |  | C_SE_NA |  | 6203 |  | P setting | MW |  |  | Active power setpoint | Pmin - Pmax, with step x
9 |  | C_SE_NA |  | 6204 |  | P decrease rate | MW/min |  |  | Active power decrease rate (MW/min) | MW/min (step 1 MW/min)
10 |  | C_SE_NA |  | 6205 |  | P raise rate | MW/min |  |  | Active power raise rate (MW/min) | MW/min (step 1 MW/min)
11 |  | M_DP_TA (TB) |  | 3002 |  | Active power control (AGC, aFRR, mFRR) | On/Off |  |  | Active power control (AGC, aFRR, mFRR) according to setpoint (feedback) | On = 1, Off = 0
12 |  | M_ME_NA |  | 1003 |  | P setting | MW |  |  | Active power setpoint (feedback) | Pmin - Pmax, with step x
13 |  | M_ME_NA |  | 1004 |  | P decrease rate | MW/min |  |  | Active power decrease rate (MW/min) (1 MW/min), (feedback) | MW/min
(step 1 MW/min)
14 |  | M_ME_NA |  | 1005 |  | P raise rate | MW/min |  |  | Active power raise rate (MW/min) (1 MW/min), (feedback) | MW/min (step 1 MW/min)
15 |  | M_ME_NA |  | 1006 |  | possible P | MW |  |  | Theoretically possible active power setpoint (AGC) | MW
16 |  | M_ME_NA |  | 1007 |  | Minimum P | MW |  |  | Theoretically possible minimum active power setpoint (AGC) | MW
QUICK LIMITATION OF ACTIVE POWER
17 |  | C_DC_NA |  | 3 |  | P emergency limit 80% | On/Off |  |  | Emergency limit 80% of active power | 10=On,01=Off
18 |  | C_DC_NA |  | 4 |  | P emergency limit 60% | On/Off |  |  | Emergency limit 60% of active power | 10=On,01=Off
19 |  | C_DC_NA |  | 5 |  | P emergency limit 40% | On/Off |  |  | Emergency limit 40% of active power | 10=On,01=Off
20 |  | C_DC_NA |  | 6 |  | P emergency limit 20% | On/Off |  |  | Emergency limit 20% of active power | 10=On,01=Off
21 |  | M_SP_TA (TB) |  | 3003 |  | P emergency limit 80% | On/Off |  |  | Emergency limit 80% of active power (feedback) | On=1,Off=0
22 |  | M_SP_TA (TB) |  | 3004 |  | P emergency limit 60% | On/Off |  |  | Emergency limit 60% of active power (feedback) | On=1,Off=0
23 |  | M_SP_TA (TB) |  | 3005 |  | P emergency limit 40% | On/Off |  |  | Emergency limit 40% of active power (feedback) | On=1,Off=0
24 |  | M_SP_TA (TB) |  | 3006 |  | P emergency limit 20% | On/Off |  |  | Emergency limit 20% of active power (feedback) | On=1,Off=0
MEASUREMENTS, INFORMATION TO OPERATOR
25 |  | M_ME_NA |  | 1008 |  | Energy park module P | MW |  |  | Active power measurement, net | MW
26 |  | M_ME_NA |  | 1009 |  | Energy park module P | MW |  |  | Active power measurement, gross | MW
27 |  | M_ME_NA |  | 1010 |  | Out of work P | MW |  |  | Nominal active power out of work | MW
ALARMS, INFORMATION TO OPERATOR
29 |  | M_SP_TA (TB) |  | 3007 |  | Limited frequency sensitive mode in the case of overfrequency | Operated/Dead |  |  | Limited frequency sensitive mode in the case of overfrequency (LFSM-O) in operation | On=1,Off=0
30 |  | M_SP_TA (TB) |  | 3008 |  | Limited frequency sensitive mode in the case of underfrequency | Operated/Dead |  |  | Limited frequency sensitive mode in the case of underfrequency (LFSM-U) in operation | On=1,Off=0
INFORMATION FOR THE FORECASTING SYSTEM
31 |  | M_ME_NA |  | 1012 |  | Wind velocity | m/sec |  |  | Wind velocity | m/sec
32 |  | M_ME_NA |  | 1013 |  | Wind direction | deg |  |  | Wind direction | deg
33 |  | M_ME_NA |  | 1014 |  | Air temperature | C |  |  | Air temperature | C
34 |  | M_ME_NA |  | 1015 |  | Air pressure | mbar (hPa) |  |  | NOT OBLIGATORY | mbar (hPa)
35 |  | M_ME_NA |  | 1016 |  | Solar intensity | W/m2 |  |  | Solar intensity | W/m2
SYNCHRONOUS MODULE
Position | Data type |  | IEC address |  | Name |  |  | Status | Description |  |  | Value
CONTROL SIGNALS AND FEEDBACK
SIGNALS REQUIRED FOR FREQUENCY STABILITY
1 | C_DC_NA |  | 1 |  | Primary control (FCR) |  |  | On/Off | Primary control (FCR) 10% |  |  | 10 = On, 01 = Off
2 | C_SE_NA |  | 6201 |  | droop |  |  | % | Droop setpoint |  |  | 2-12%, with step 1%
3 | C_SE_NA |  | 6202 |  | frequency controller dead band |  |  | mHz | Frequency controller dead band setpoint |  |  | 0-500 mHz, with step 10 mHz
4 | M_DP_TA (TB) |  | 3001 |  | Primary control (FCR) |  |  | On/Off | Primary control (FCR) 10% (feedback) |  |  | On = 1, Off = 0
5 | M_ME_NA |  | 1001 |  | droop |  |  | % | Droop setpoint (feedback) |  |  | 2-12%, with step 1%
6 | M_ME_NA |  | 1002 |  | frequency controller dead band |  |  | mHz | Frequency controller dead band setpoint (feedback) |  |  | 0-500 mHz, with step 10 mHz
SIGNALS REQUIRED TO ENSURE FREQUENCY STABILITY OR REGIONAL STABILITY
ACTIVE POWER CONTROL BY SETTING WITH RAISE AND DECREASE RATE
7 | C_DC_NA |  | 2 |  | Active power control (AGC, aFRR, mFRR) |  |  | On/Off | Active power control (AGC, aFRR, mFRR) according to setpoint (must also function as a limiter) |  |  | 10 = On, 01 = Off
8 | C_SE_NA |  | 6203 |  | P setting |  |  | MW | Active power setpoint |  |  | Pmin - Pmax, with step x
9 | C_SE_NA |  | 6204 |  | P decrease rate |  |  | MW/min | Active power ramp rate, decrease (MW/min) (IF IT IS TECHNICALLY POSSIBLE TO MODIFY) |  |  | MW/min (step 1 MW/min)
10 | C_SE_NA |  | 6205 |  | P raise rate |  |  | MW/min | Active power ramp rate, raising (MW/min) (IF IT IS TECHNICALLY POSSIBLE TO MODIFY) |  |  | MW/min (step 1 MW/min)
11 | M_DP_TA (TB) |  | 3002 |  | Active power control (AGC, aFRR, mFRR) |  |  | On/Off | Active power control (AGC, aFRR, mFRR) according to setpoint (feedback) |  |  | On = 1, Off = 0
12 | M_ME_NA |  | 1003 |  | P setting |  |  | MW | Active power setpoint (feedback) |  |  | Pmin - Pmax, with step x
13 | M_ME_NA |  | 1004 |  | P decrease rate |  |  | MW/min | Active power ramp rate, decrease (1MW/min) (IF IT IS TECHNICALLY POSSIBLE TO MODIFY) (feedback) |  |  | MW/min
(step 1 MW/min)
14 | M_ME_NA |  | 1005 |  | P raise rate |  |  | MW/min | Active power ramp rate, raising (1MW/min) (feedback) (IF IT IS TECHNICALLY POSSIBLE TO MODIFY) |  |  | MW/min (step 1 MW/min)
15 | M_ME_NA |  | 1006 |  | possible P |  |  | MW | Theoretically possible active power setpoint (AGC) |  |  | MW
16 | M_ME_NA |  | 1007 |  | Minimum P |  |  | MW | Theoretically possible minimum active power setpoint (AGC) |  |  | MW
MEASUREMENTS, INFORMATION TO OPERATOR
17 | M_ME_NA |  | 1008 |  | Synchronous module P |  |  | MW | Active power measurement, net |  |  | MW
18 | M_ME_NA |  | 1009 |  | Synchronous module P |  |  | MW | Active power measurement, gross |  |  | MW
19 | M_ME_NA |  | 1010 |  | Out of work P |  |  | MW | Nominal active power out of work |  |  | MW
ALARMS, INFORMATION TO OPERATOR
21 | M_SP_TA (TB) |  | 3003 |  | Limited frequency sensitive mode in the case of overfrequency |  |  | Operated/Dead | Limited frequency sensitive mode in the case of overfrequency (LFSM-O) in operation |  |  | On=1,Off=0
22 | M_SP_TA (TB) |  | 3004 |  | Limited frequency sensitive mode in the case of underfrequency |  |  | Operated/Dead | Limited frequency sensitive mode in the case of underfrequency (LFSM-U) in operation |  |  | On=1,Off=0